EWB Minutes 3/23/11

EIA says our observation about the overflow valve in the FPS spring is wrong and that the water is leaking from the ARV. However, we found pictures of the cattle trough with water and the ARV not leaking.

We can pay Milton to go to Papachacra on April 15th. We have to put together questions to ask him.

RAM and Wind pumps are being used already but we’ll need to look more into the RAM pump since we saw that it only pushes 10% of the volume.

We could possibly use RAM pumps on the tree spring and/ or the PRV on the main line to get equal pressure.

David is going to ask EIA why they think the tree spring is irrelevant when we found the flow to be 17,000 L/day.

To Do:

Research RAM Pumps

Look at box/ reservoir construction

Pipe/ pipe laying calculations (question about how much flow/ pressure goes into each branch.)

Model PRV with Tree Spring in EPANET

Alex  needs to finish the website

Questions:

How high does the water level get at night in the treatment tanks?